**FELT MATS**

**KNAUF INSULATION THERMO-TEK FM 040**

**Type of Insulation:**

Mineral wool felt mat for the insulation of piping, elbows and fittings, air ducts, non-regular units and for fill material of mattresses.

The felt mat must have certifications and CE marking in accordance with EN 13162.

**Facing:**

The felt mat shall have no own facing.

**Description:**

Mineral wool felt mat, with low binder content. The mineral wool felt mat shall use a mainly bio-based binder, e.g. Ecose Technology, contain no added formaldehyde and be certified under Eurofins Gold Indoor Air Comfort quality standards or equivalent.

**Main characteristics:**

1. Eurofins

Certification Indoor Air Comfort: Gold Standard

2. Fire

The felt mats shall be non-combustible with the following reaction to fire according to
EN 13501-1: A1.

3. Thermal

The thermal conductivity λ-value shall be according to EN 12667:

0,037 W/(mK) at 10 °C

4. Chemicals

AS quality, according to EN ISO 12624: content of chlorides less than 10 ppm.

5. Density

Density shall be 40 kg/m³, according to EN ISO 29470.

6. Dimensional tolerances

The dimensional tolerance class shall be T2, according to EN 13162.

7. Other certifications

RAL certification.

7. Other requirements

Water vapour diffusion resistance coefficient µ-value, according to EN 13162: µ= 1.

Water absorption, according to EN ISO 29767: maximum 1 kg/m².

Melting point of fibres, according to DIN 4102-17: ≥ 1000 °C.

Longitudinal air flow resistance, according to EN 29053: ≥ 5 kPa∙s/m²

**EN designation code:**

MW-EN13162-T2-WS-AF5

**Standard Dimensions:**

Felt mat length shall be: from 3000 mm to 10000 mm, depending on the thickness.

Felt mat width shall be 500 or 1000 mm.

Felt mat thickness shall be: 30, 40, 50, 60, 80, 100 mm.

**FELT MATS**

**KNAUF INSULATION THERMO-TEK FM 050**

**Type of Insulation:**

Mineral wool felt mat for the insulation of piping, elbows and fittings, air ducts, non-regular units and for fill material of mattresses.

The felt mat must have certifications and CE marking in accordance with EN 13162.

**Facing:**

The felt mat shall have no own facing.

**Description:**

Mineral wool felt mat, with low binder content. The mineral wool felt mat shall use a mainly bio-based binder, e.g. Ecose Technology, contain no added formaldehyde and be certified under Eurofins Gold Indoor Air Comfort quality standards or equivalent.

**Main characteristics:**

1. Eurofins

Certification Indoor Air Comfort: Gold Standard

2. Fire

The felt mats shall be non-combustible with the following reaction to fire according to
EN 13501-1: A1.

3. Thermal

The thermal conductivity λ-value shall be according to EN 12667:

0,035 W/(mK) at 10 °C

4. Chemicals

AS quality, according to EN 13468: content of chlorides less than 10 ppm.

5. Dimensional tolerances

The dimensional tolerance class shall be T2, according to EN 13162.

6. Other requirements

Water vapour diffusion resistance coefficient µ-value, according to EN 13162: µ= 1.

Water absorption, according to EN 1609: maximum 1 kg/m².

Melting point of fibres, according to DIN 4102-17: ≥ 1000 °C.

Longitudinal air flow resistance, according to EN 29053: ≥ 10 kPa∙s/m²

**EN designation code:**

MW-EN13162-T2-WS-AF10

**Standard Dimensions:**

Felt mat length shall be: from 3000 mm to 10000 mm, depending on the thickness.

Felt mat width shall be 500 or 1000 mm.

Felt mat thickness shall be: 30, 40, 50, 60, 80, 100 mm.

**FELT MATS**

**KNAUF INSULATION THERMO-TEK FM 060**

**Type of Insulation:**

Mineral wool felt mat for the insulation of piping, elbows and fittings, air ducts, non-regular units and for fill material of mattresses.

The felt mat must have certifications and CE marking in accordance with EN 13162.

**Facing:**

The felt mat shall have no own facing.

**Description:**

Mineral wool felt mat, with low binder content. The mineral wool felt mat shall use a mainly bio-based binder, e.g. Ecose Technology, contain no added formaldehyde and be certified under Eurofins Gold Indoor Air Comfort quality standards or equivalent.

**Main characteristics:**

1. Eurofins

Certification Indoor Air Comfort: Gold Standard

2. Fire

The felt mats shall be non-combustible with the following reaction to fire according to
EN 13501-1: A1.

3. Thermal

The thermal conductivity λ-value shall be according to EN 12667:

0,035 W/(mK) at 10 °C

4. Chemicals

AS quality, according to EN 13468: content of chlorides less than 10 ppm.

5. Dimensional tolerances

The dimensional tolerance class shall be T2, according to EN 13162.

6. Other requirements

Water vapour diffusion resistance coefficient µ-value, according to EN 13162: µ= 1.

Water absorption, according to EN 1609: maximum 1 kg/m².

Melting point of fibres, according to DIN 4102-17: ≥ 1000 °C.

Longitudinal air flow resistance, according to EN 29053: ≥ 15 kPa∙s/m²

**EN designation code:**

MW-EN13162-T2-WS-AF15

**Standard Dimensions:**

Felt mat length shall be: from 3000 mm to 10000 mm, depending on the thickness.

Felt mat width shall be 500 or 1000 mm.

Felt mat thickness shall be: 30, 40, 50, 60, 80, 100 mm.