**HIGH TEMPERATURE BOARDS**

**KNAUF INSULATION POWER-TEK BD 450 ALU**

**Type of Insulation:**

Mineral wool board for the insulation of vessel walls, columns, power plant boilers, furnaces, flue gas ducts.

The board must have certifications and CE marking in accordance with EN 14303.

**Facing:**

The board shall a have glass fibre reinforced aluminium foil on one side.

**Description:**

Board for high temperature applications with a glass fibre reinforced aluminium foil on one side. The mineral wool board shall use a mainly bio-based binder, e.g. Ecose Technology, contain no added formaldehyde and be certified under Eurofins Gold Indoor Air Comfort quality standards or equivalent.

**Main characteristics:**

1. Eurofins

Certification Indoor Air Comfort: Gold Standard

2. Fire

The board shall be non-combustible with the following reaction to fire according to   
EN 13501-1: A1.

3. Thermal

The thermal conductivity λ-value shall be according to EN 12667:

0,037 W/(mK) at 10 °C

0,041 W/(mK) at 50 °C

0,048 W/(mK) at 100°C

0,071 W/(mK) at 200 °C

0,108 W/(mK) at 300 °C

0,157 W/(mK) at 400 °C

0,186 W/(mK) at 500 °C

The maximum service temperature is measured according to EN 14706 and shall be minimum   
450 °C.

4. Chemicals

AS quality, according to EN 13468: content of chlorides less than 10 ppm.

5. Dimensional tolerances

The dimensional tolerance class shall be T5, according to EN 14303.

6. Other requirements

Water vapour diffusion resistance, according to EN 12086: Sd ≥ 200 m.

Water absorption, according to EN 1609: maximum 1 kg/m².

Melting point of fibres, according to DIN 4102-17: ≥ 1000 °C.

Longitudinal air flow resistance, according to EN 29053: ≥ 10 kPa∙s/m²

**EN designation code:**

MW-EN14303-T5-ST(+)450-WS1-MV2-CL10

**Standard Dimensions:**

High temperature board length shall be 1000 mm.

High temperature board width shall be 600 mm.

High temperature board thickness shall be: 40, 50, 60, 70, 80, 90, 100 mm (maximum possible thickness 250 mm).

**HIGH TEMPERATURE BOARDS**

**KNAUF INSULATION POWER-TEK BD 550 ALU**

**Type of Insulation:**

Mineral wool board for the insulation of vessel walls, columns, power plant boilers, furnaces, flue gas ducts.

The board must have certifications and CE marking in accordance with EN 14303.

**Facing:**

The board shall a have glass fibre reinforced aluminium foil on one side.

**Description:**

Board for high temperature applications with a glass fibre reinforced aluminium foil on one side. The mineral wool board shall use a mainly bio-based binder, e.g. Ecose Technology, contain no added formaldehyde and be certified under Eurofins Gold Indoor Air Comfort quality standards or equivalent.

**Main characteristics:**

1. Eurofins

Certification Indoor Air Comfort: Gold Standard

2. Fire

The board shall be non-combustible with the following reaction to fire according to   
EN 13501-1: A1.

3. Thermal

The thermal conductivity λ-value shall be according to EN 12667:

0,040 W/(mK) at 50 °C

0,046 W/(mK) at 100°C

0,067 W/(mK) at 200 °C

0,094 W/(mK) at 300 °C

0,130 W/(mK) at 400 °C

0,176 W/(mK) at 500 °C

0,204 W/(mK) at 550 °C

The maximum service temperature is measured according to EN 14706 and shall be minimum   
550 °C.

4. Chemicals

AS quality, according to EN 13468: content of chlorides less than 10 ppm.

5. Dimensional tolerances

The dimensional tolerance class shall be T5, according to EN 14303.

6. Other requirements

Water vapour diffusion resistance, according to EN 12086: Sd ≥ 200 m.

Water absorption, according to EN 1609: maximum 1 kg/m².

Melting point of fibres, according to DIN 4102-17: ≥ 1000 °C.

Longitudinal air flow resistance, according to EN 29053: ≥ 15 kPa∙s/m²

**EN designation code:**

MW-EN14303-T5-ST(+)550-WS1-MV2-CL10

**Standard Dimensions:**

High temperature board length shall be 1000 mm.

High temperature board width shall be 600 mm.

High temperature board thickness shall be: 30, 40, 50, 60, 70, 80, 90, 100 mm (maximum possible thickness 250 mm).

**HIGH TEMPERATURE BOARDS**

**KNAUF INSULATION POWER-TEK BD 620 ALU**

**Type of Insulation:**

Mineral wool high temperature board for the insulation of vessel walls, columns, power plant boilers, furnaces, flue gas ducts.

The board must have certifications and CE marking in accordance with EN 14303.

**Facing:**

The board shall a have glass fibre reinforced aluminium foil on one side.

**Description:**

Board for high temperature applications with a glass fibre reinforced aluminium foil on one side. The mineral wool board shall use a mainly bio-based binder, e.g. Ecose Technology, contain no added formaldehyde and be certified under Eurofins Gold Indoor Air Comfort quality standards or equivalent.

**Main characteristics:**

1. Eurofins

Certification Indoor Air Comfort: Gold Standard

2. Fire

The board shall be non-combustible with the following reaction to fire according to   
EN 13501-1: A1.

3. Thermal

The thermal conductivity λ-value shall be according to EN 12667:

0,039 W/(mK) at 50 °C

0,046 W/(mK) at 100°C

0,065 W/(mK) at 200 °C

0,089 W/(mK) at 300 °C

0,120 W/(mK) at 400 °C

0,160 W/(mK) at 500 °C

0,209 W/(mK) at 600 °C

The maximum service temperature is measured according to EN 14706 and shall be minimum   
620 °C.

4. Chemicals

AS quality, according to EN 13468: content of chlorides less than 10 ppm.

5. Dimensional tolerances

The dimensional tolerance class shall be T5, according to EN 14303.

6. Other requirements

Water vapour diffusion resistance, according to EN 12086: Sd ≥ 200 m.

Water absorption, according to EN 1609: maximum 1 kg/m².

Melting point of fibres, according to DIN 4102-17: ≥ 1000 °C.

Longitudinal air flow resistance, according to EN 29053: ≥ 15 kPa∙s/m²

**EN designation code:**

MW-EN14303-T5-ST(+)620-WS1-MV2-CL10

**Standard Dimensions:**

High temperature board length shall be 1000 mm.

High temperature board width shall be 600 mm.

High temperature board thickness shall be: 30, 40, 50, 60, 70, 80, 90, 100 mm (maximum possible thickness 250 mm).

**HIGH TEMPERATURE BOARDS**

**KNAUF INSULATION POWER-TEK BD 640 ALU**

**Type of Insulation:**

Mineral wool high temperature board for the insulation of vessel walls, columns, power plant boilers, furnaces, flue gas ducts.

The board must have certifications and CE marking in accordance with EN 14303.

**Facing:**

The board shall a have glass fibre reinforced aluminium foil on one side.

**Description:**

Board for high temperature applications with a glass fibre reinforced aluminium foil on one side. The mineral wool board shall use a mainly bio-based binder, e.g. Ecose Technology, contain no added formaldehyde and be certified under Eurofins Gold Indoor Air Comfort quality standards or equivalent.

**Main characteristics:**

1. Eurofins

Certification Indoor Air Comfort: Gold Standard

2. Fire

The board shall be non-combustible with the following reaction to fire according to   
EN 13501-1: A1.

3. Thermal

The thermal conductivity λ-value shall be according to EN 12667:

0,040 W/(mK) at 50 °C

0,049 W/(mK) at 100°C

0,067 W/(mK) at 200 °C

0,092 W/(mK) at 300 °C

0,123 W/(mK) at 400 °C

0,163 W/(mK) at 500 °C

0,215 W/(mK) at 600 °C

The maximum service temperature is measured according to EN 14706 and shall be minimum   
640 °C.

4. Chemicals

AS quality, according to EN 13468: content of chlorides less than 10 ppm.

5. Dimensional tolerances

The dimensional tolerance class shall be T5, according to EN 14303.

6. Other requirements

Water vapour diffusion resistance, according to EN 12086: Sd ≥ 200 m.

Water absorption, according to EN 1609: maximum 1 kg/m².

Melting point of fibres, according to DIN 4102-17: ≥ 1000 °C.

Longitudinal air flow resistance, according to EN 29053: ≥ 15 kPa∙s/m²

**EN designation code:**

MW-EN14303-T5-ST(+)640-WS1-MV2-CL10

**Standard Dimensions:**

High temperature board length shall be 1000 mm.

High temperature board width shall be 600 mm.

High temperature board thickness shall be: 30, 40, 50, 60, 70, 80, 90, 100 mm (maximum possible thickness 250 mm).

**HIGH TEMPERATURE BOARDS**

**KNAUF INSULATION POWER-TEK BD 660 ALU**

**Type of Insulation:**

Mineral wool high temperature board for the insulation of vessel walls, columns, power plant boilers, furnaces, flue gas ducts.

The board must have certifications and CE marking in accordance with EN 14303.

**Facing:**

The board shall a have glass fibre reinforced aluminium foil on one side.

**Description:**

Board for high temperature applications with a glass fibre reinforced aluminium foil on one side. The mineral wool board shall use a mainly bio-based binder, e.g. Ecose Technology, contain no added formaldehyde and be certified under Eurofins Gold Indoor Air Comfort quality standards or equivalent.

**Main characteristics:**

1. Eurofins

Certification Indoor Air Comfort: Gold Standard

2. Fire

The board shall be non-combustible with the following reaction to fire according to   
EN 13501-1: A1.

3. Thermal

The thermal conductivity λ-value shall be according to EN 12667:

0,039 W/(mK) at 50 °C

0,044 W/(mK) at 100°C

0,060 W/(mK) at 200 °C

0,078 W/(mK) at 300 °C

0,102 W/(mK) at 400 °C

0,132 W/(mK) at 500 °C

0,169 W/(mK) at 600 °C

The maximum service temperature is measured according to EN 14706 and shall be minimum   
660 °C.

4. Chemicals

AS quality, according to EN 13468: content of chlorides less than 10 ppm.

5. Dimensional tolerances

The dimensional tolerance class shall be T5, according to EN 14303.

6. Other requirements

Water vapour diffusion resistance, according to EN 12086: Sd ≥ 200 m.

Water absorption, according to EN 1609: maximum 1 kg/m².

Melting point of fibres, according to DIN 4102-17: ≥ 1000 °C.

Longitudinal air flow resistance, according to EN 29053: ≥ 25 kPa∙s/m²

**EN designation code:**

MW-EN14303-T5-ST(+)660-WS1-MV2-CL10

**Standard Dimensions:**

High temperature board length shall be 1000 mm.

High temperature board width shall be 600 mm.

High temperature board thickness shall be: 20, 30, 40, 50, 60, 70, 80, 90, 100 mm (maximum possible thickness 250 mm).

**HIGH TEMPERATURE BOARDS**

**KNAUF INSULATION POWER-TEK BD 680 ALU**

**Type of Insulation:**

Mineral wool high temperature board for the insulation of vessel walls, columns, power plant boilers, furnaces, flue gas ducts.

The board must have certifications and CE marking in accordance with EN 14303.

**Facing:**

The board shall a have glass fibre reinforced aluminium foil on one side.

**Description:**

Board for high temperature applications with a glass fibre reinforced aluminium foil on one side. The mineral wool board shall use a mainly bio-based binder, e.g. Ecose Technology, contain no added formaldehyde and be certified under Eurofins Gold Indoor Air Comfort quality standards or equivalent.

**Main characteristics:**

1. Eurofins

Certification Indoor Air Comfort: Gold Standard

2. Fire

The board shall be non-combustible with the following reaction to fire according to   
EN 13501-1: A1.

3. Thermal

The thermal conductivity λ-value shall be according to EN 12667:

0,040 W/(mK) at 50 °C

0,045 W/(mK) at 100°C

0,059 W/(mK) at 200 °C

0,075 W/(mK) at 300 °C

0,096 W/(mK) at 400 °C

0,121 W/(mK) at 500 °C

0,153 W/(mK) at 600 °C

0,180 W/(mK) at 650 °C

The maximum service temperature is measured according to EN 14706 and shall be minimum   
680 °C.

4. Chemicals

AS quality, according to EN 13468: content of chlorides less than 10 ppm.

5. Dimensional tolerances

The dimensional tolerance class shall be T5, according to EN 14303.

6. Other requirements

Water vapour diffusion resistance, according to EN 12086: Sd ≥ 200 m.

Water absorption, according to EN 1609: maximum 1 kg/m².

Melting point of fibres, according to DIN 4102-17: ≥ 1000 °C.

Longitudinal air flow resistance, according to EN 29053: ≥ 30 kPa∙s/m²

**EN designation code:**

MW-EN14303-T5-ST(+)680-WS1-MV2-CL10

**Standard Dimensions:**

High temperature board length shall be 1000 mm.

High temperature board width shall be 600 mm.

High temperature board thickness shall be: 20, 30, 40, 50, 60, 70, 80, 90, 100 mm (maximum possible thickness 200 mm).

**HIGH TEMPERATURE BOARDS**

**KNAUF INSULATION POWER-TEK BD 700 ALU**

**Type of Insulation:**

Mineral wool high temperature board for the insulation of vessel walls, columns, power plant boilers, furnaces, flue gas ducts.

The board must have certifications and CE marking in accordance with EN 14303.

**Facing:**

The board shall a have glass fibre reinforced aluminium foil on one side.

**Description:**

Board for high temperature applications with a glass fibre reinforced aluminium foil on one side. The mineral wool board shall use a mainly bio-based binder, e.g. Ecose Technology, contain no added formaldehyde and be certified under Eurofins Gold Indoor Air Comfort quality standards or equivalent.

**Main characteristics:**

1. Eurofins

Certification Indoor Air Comfort: Gold Standard

2. Fire

The board shall be non-combustible with the following reaction to fire according to   
EN 13501-1: A1.

3. Thermal

The thermal conductivity λ-value shall be according to EN 12667:

0,041 W/(mK) at 50 °C

0,045 W/(mK) at 100°C

0,059 W/(mK) at 200 °C

0,075 W/(mK) at 300 °C

0,095 W/(mK) at 400 °C

0,119 W/(mK) at 500 °C

0,147 W/(mK) at 600 °C

0,178 W/(mK) at 700 °C

The maximum service temperature is measured according to EN 14706 and shall be minimum   
700 °C.

4. Chemicals

AS quality, according to EN 13468: content of chlorides less than 10 ppm.

5. Dimensional tolerances

The dimensional tolerance class shall be T5, according to EN 14303.

6. Other requirements

Water vapour diffusion resistance, according to EN 12086: Sd ≥ 200 m.

Water absorption, according to EN 1609: maximum 1 kg/m².

Melting point of fibres, according to DIN 4102-17: ≥ 1000 °C.

Longitudinal air flow resistance, according to EN 29053: ≥ 30 kPa∙s/m²

**EN designation code:**

MW-EN14303-T5-ST(+)700-WS1-MV2-CL10

**Standard Dimensions:**

High temperature board length shall be 1000 mm.

High temperature board width shall be 600 mm.

High temperature board thickness shall be: 20, 30, 40, 50, 60, 70, 80, 90, 100 mm (maximum possible thickness 160 mm).